


Longcross DC Model issues

ANCILLARY BLOCK.

1. Escape stair showing through roof. Ancillary block.  
   Parapet wall drops



Birds eye views

Larger 3D

Diagram

Description automatically generated

Wall sweep Profile 13 above Roof

Some Internal Door heads above ceiling?   
L1 shown below:

L2 Same issue

Diagram

Description automatically generated

Diagram

Description automatically generatedGraphical user interface, application, Word

Description automatically generated

Double floor around Lift Shafts at L0

Also Double wall.

A drawing of a basketball hoop

Description automatically generated with low confidence

No Door shown on Passenger Lift door on second floor

ENERGY CENTRE.

Diagram

Description automatically generatedDiagram

Description automatically generated

Structural Bracing currently clashes with plant…

S. Eng to Relocate to adjacent Bay against Partition.


Stair 02 (Energy Centre)  
Adjacent to lift shaft, access up to roof level.

Lift pit to align with shaft.

Diagram

Description automatically generated

Internal Partition crashes though Lobby



Stair 02 (Energy Centre)  
should go up to roof level.

Stair 01 (energy Centre)

Stops at Level 2 with Ladder ‘escape only’ from roof level.

Lift pit to align with shaft.